## Electrification Calculator
Building Electrification Calculator
Date: | 2020-11-09 |  |  | = Input Cell
General Project Inputs | [6 empty] | Utility Rates
Project Name |  | EXAMPLE Office Building
Location |  | Lakewood, CO |  |  |  |  | Rate Type |  | Commercial
Building Area |  | 28000
Building Type |  | Office |  |  |  |  | Baseline Rate
[7 empty] | Utility Rate Structure |  | Xcel Energy Secondary General (no Time of Use)
Existing System Type |  | Packaged Roof Top Units
Existing System Heating Efficiency |  | 80% | [6 empty] | Baseline Utility Rates
Replacement System Type |  | Single Zone RTU Packaged Unit with Heat Pump | [6 empty] | $/Peak kW | $/kWh on Peak | $/kWh off Peak
Number of units being replaced |  | 9 | [5 empty] | Summer | 25.07 | 0.0455 | 0.0455
Average cooling unit capacity (tons) |  | 10 | [5 empty] | Winter | 20.52 | 0.0455 | 0.0455
Include cooling savings? |  | No | [5 empty] | Summer Months: | Jun to Sep
Existing Cooling Efficiency (SEER) |  | 10.1
Project Costs
Project type (NC = New Construction, EOL = End of Life, Retrofit) |  |  |  | EOL |  |  | Proposed Rate
[7 empty] | Utility Rate Structure |  | Xcel Energy Primary General (Time of Use)
*Both options assume high efficiency equipment |  |  | Heat Pump | Natural Gas
Central heating/cooling system (including install) |  |  | 234000 | 234000 |  |  |  |  | Test Rate Reductions
Average cost per ton |  |  | 2600 | 2600 |  |  |  |  | $/Peak kW | $/kWh on Peak | $/kWh off Peak
Tank type domestic hot water heater |  |  | 4200 | 2600 |  |  |  | Summer | 0% | 0% | 0%
Electrical modification |  |  | 3000 |  |  |  |  | Winter | 0% | 0% | 0%
Natural gas connection and piping (NC only) |  |  |  | 21000
Total implementation cost |  |  | 241200 | 236600 |  |  |  |  | Proposed Utility Rates with Reduction
Rebate amount |  |  | 0 | [5 empty] | $/Peak kW | $/kWh on Peak | $/kWh off Peak
Total implementation cost with rebate |  |  | 241200 | 236600 |  |  |  | Summer | 23.48 | 0.0534 | 0.0389
[8 empty] | Winter | 18.34 | 0.0534 | 0.0389
Delta in Cost for Heat Pump vs. Natural Gas |  |  | $ Delta | % Delta
Before Rebate |  |  | 4600 | 1.944%
After Rebate |  |  | 4600 | 1.944%
Operating Cost Summary
|  | Gas Heat - Baseline | HP - Current Elec Rate | HP - New Elec Rate | Change w/ Current Elec Rate | Change w/ New Elec Rate | % Change w/ Current Elec Rate | % Change w/ New Elec Rate
| Natural Gas Cost ($/yr) | 4983.08 | 0 | 0 | -4983.08 | -4983.08
| Elec Heat Cost ($/yr) | 0 | 5569.2445 | 5237.1323 | 5569.2445 | 5237.1323 | 111.8% | 105.1%
| Elec Non-Heat Cost ($/yr) | 50047.95 | 50047.95 | 47158.1232 | 0 | -2889.8268 | 0% | -5.774%
| Total Elec Cost ($/yr) | 50047.95 | 55617.1945 | 52395.2555 | 5569.2445 | 2347.3055
| Total Utility Cost ($/yr) | 55031.03 | 55617.1945 | 52395.2555 | 586.1645 | -2635.7745 | 1.065% | -4.79%
|  |  | Overall simple payback |  | NA | 1.7452 | Years
Economic Summary
|  | Gas Heat - Baseline | HP - Current Elec Rate | HP - New Elec Rate | Change w/ Current Elec Rate | Change w/ New Elec Rate | % Change w/ Current Elec Rate | % Change w/ New Elec Rate
| Net Present Cost (15 yrs) | 761965.3857 | 774871.24 | 743955.3299 | 12905.8543 | -18010.0559 | 1.694% | -2.364%
Whole Building Heating - Natural Gas to Electric Heat Conversion
[15 empty] | Current Rates |  |  |  |  | New Rates
Season | Month | Season | Baseline Natural Gas Use (Therms) | Baseline Natural Gas Cost ($) | $/ therm | Total Natural Gas kBtu | New System Efficiency | Total Heating Use in kWh | Total Heating Use in kBtu | % of Heating kWh On Peak | Heating Load Factor | Avg. Heating Peak Demand in kW | % of Heating Peak that Adds to Existing Peak | Avg. Addition to Existing Peak (kW/mo) | Total Cost of Electric Heating kWh | Total Cost of Electric Heating kW | Total Cost of Electric Heating ($) | Change in Heating Cost ($) | % Change in Heating Cost | Total Cost of Electric Heating kWh | Total Cost of Electric Heating kW | Total Cost of Electric Heating ($) | Change in Heating Cost ($) | % Change in Heating Cost
Winter | January | Winter | 1363 | 895.28 | 0.65685 | 136300 | 230% | 13890.7952 | 47395.3933 | 45% | 44.79% | 43.0751 | 60% | 25.845 | 632.0312 | 530.3401 | 1162.3713 | 267.0913 | 29.83% | 630.9894 | 473.9979 | 1104.9873 | 209.7073 | 23.42%
Winter | February | Winter | 859 | 580.19 | 0.67542 | 85900 | 243% | 8286.02 | 28271.9004 | 35% | 45.24% | 25.4401 | 50% | 12.72 | 377.0139 | 261.015 | 638.0289 | 57.8389 | 9.969% | 364.3777 | 233.2853 | 597.663 | 17.473 | 3.012%
Winter | March | Winter | 548 | 376.94 | 0.68785 | 54800 | 269% | 4775.1538 | 16292.8249 | 30% | 28.08% | 23.6152 | 40% | 9.4461 | 217.2695 | 193.8333 | 411.1028 | 34.1628 | 9.063% | 206.5254 | 173.2408 | 379.7662 | 2.8262 | 0.7498%
Winter | April | Winter | 481 | 315.2 | 0.6553 | 48100 | 303.7% | 3712.8469 | 12668.2337 | 30% | 26.24% | 19.6539 | 30% | 5.8962 | 168.9345 | 120.9892 | 289.9237 | -25.2763 | -8.019% | 160.5806 | 108.1356 | 268.7162 | -46.4838 | -14.75%
Winter | May | Winter | 390 | 264.94 | 0.67933 | 39000 | 347% | 2634.4759 | 8988.8316 | 30% | 18.33% | 19.96 | 20% | 3.992 | 119.8687 | 81.9158 | 201.7844 | -63.1556 | -23.84% | 113.9411 | 73.2132 | 187.1543 | -77.7857 | -29.36%
Summer | June | Summer | 143 | 125.04 | 0.87441 | 14300 | 386% | 868.376 | 2962.899 | 30% | 19.15% | 6.2969 | 10% | 0.62969 | 39.5111 | 15.7864 | 55.2975 | -69.7425 | -55.78% | 37.5573 | 14.7852 | 52.3424 | -72.6976 | -58.14%
Summer | July | Summer | 99 | 101.27 | 1.0229 | 9900 | 412% | 563.2446 | 1921.7907 | 30% | 24.23% | 3.2289 | 10% | 0.32289 | 25.6276 | 8.0949 | 33.7226 | -67.5474 | -66.7% | 24.3603 | 7.5815 | 31.9419 | -69.3281 | -68.46%
Summer | August | Summer | 139 | 124.08 | 0.89266 | 13900 | 403.3% | 807.811 | 2756.2512 | 30% | 19.22% | 5.8376 | 10% | 0.58376 | 36.7554 | 14.6349 | 51.3903 | -72.6897 | -58.58% | 34.9378 | 13.7068 | 48.6446 | -75.4354 | -60.8%
Summer | September | Summer | 145 | 128.15 | 0.88379 | 14500 | 360% | 944.1143 | 3221.3181 | 30% | 13.63% | 9.6171 | 30% | 2.8851 | 42.9572 | 72.3299 | 115.2871 | -12.8629 | -10.04% | 40.8329 | 67.7426 | 108.5755 | -19.5745 | -15.27%
Winter | October | Winter | 386 | 274.02 | 0.7099 | 38600 | 312.3% | 2896.8637 | 9884.0989 | 30% | 28% | 14.368 | 40% | 5.7472 | 131.8073 | 117.9322 | 249.7395 | -24.2805 | -8.861% | 125.2894 | 105.4033 | 230.6927 | -43.3273 | -15.81%
Winter | November | Winter | 1243 | 782.83 | 0.62979 | 124300 | 264.7% | 11008.5716 | 37561.2462 | 35% | 34.61% | 44.1788 | 50% | 22.0894 | 500.89 | 453.2747 | 954.1647 | 171.3347 | 21.89% | 484.1019 | 405.1198 | 889.2217 | 106.3917 | 13.59%
Winter | December | Winter | 1658 | 1015.14 | 0.61227 | 165800 | 230% | 16897.2403 | 57653.3838 | 45% | 45.32% | 51.7875 | 60% | 31.0725 | 768.8244 | 637.6073 | 1406.4317 | 391.2917 | 38.55% | 767.5571 | 569.8693 | 1337.4264 | 322.2864 | 31.75%
| Total Annual |  | 7454 | 4983.08 | 0.66851 | 745400 | --- | 67285.5134 | 229578.1719 | --- | --- | 22.2549 | --- | --- | 3061.4909 | 2507.7536 | 5569.2445 | 586.1645 | 11.76% | 2991.051 | 2246.0813 | 5237.1323 | 254.0523 | 5.098%
| Intensity (per sq.ft./yr) |  | 0.26621 | 0.17797 | --- | 26.6214 | --- | 2.4031 | 8.1992 | --- | --- | 0.00079482 | --- | --- | 0.10934 | 0.089563 | 0.1989 | 0.020934 | --- | 0.10682 | 0.080217 | 0.18704 | 0.0090733 | ---
| Cost/kBtu |  | --- | 0.0066851 | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | 0.0074715 | --- | --- | --- | --- | 0.0070259 | --- | ---
Electricity Costs & Cooling Efficiency Savings Calculations
This section calculates the non-heating electric costs with different utility rates with the option to incorporate cooling savings.
Replacement Cooling Efficiency (SEER): |  |  | 12
Reduction in Cooling Energy: |  |  | 15.83%
[17 empty] | Current Rates | [5 empty] | New Rates
Season | Month | Season | Total Electricity Use (kWh) | Total Electricity Demand (kW) | % of kWh Assumed to be Peak | Baseline Electricity Cost | Aggregate $/ kWh | Total Electric kBtu | Cooling % of Electric Total | Baseline Cooling Energy Use (kWh) | Baseline Cooling Electric Peak (kW) | Cooling Energy Savings (kWh) | Cooling Demand Savings (kW) | New Total Electricity Use (KWh) | New Total Electricity Demand (kW) | New Electric kBtu | New Electric Energy Cost ($) | New Electric Demand Cost ($) | New Electric Cost ($/Yr) | Change in Electric Cost ($/Yr) | New Aggregate Electric Cost ($/Yr) | % Change in Total Electric Cost | New Electric Energy Cost ($) | New Electric Demand Cost ($) | New Electric Cost ($/Yr) | Change in Electric Cost ($/Yr) | New Aggregate Electric Cost ($/Yr) | % Change in Total Electric Cost
Winter | January | Winter | 30240 | 99 | 44.84% | 3407.4 | 0.11268 | 103178.88 | 0% | 0 | 0 | 0 | 0 | 30240 | 99 | 103178.88 | 1375.92 | 2031.48 | 3407.4 | 0 | 0.11268 | 0% | 1372.9714 | 1815.66 | 3188.6314 | -218.7686 | 0.10544 | -6.42%
Winter | February | Winter | 32480 | 108 | 44.69% | 3694 | 0.11373 | 110821.76 | 0% | 0 | 0 | 0 | 0 | 32480 | 108 | 110821.76 | 1477.84 | 2216.16 | 3694 | 0 | 0.11373 | 0% | 1473.9311 | 1980.72 | 3454.6511 | -239.3489 | 0.10636 | -6.479%
Winter | March | Winter | 33600 | 112 | 43.99% | 3827.04 | 0.1139 | 114643.2 | 3% | 1008 | 3.36 | 159.6 | 0.532 | 33600 | 112 | 114643.2 | 1528.8 | 2298.24 | 3827.04 | 0 | 0.1139 | 0% | 1521.3513 | 2054.08 | 3575.4313 | -251.6087 | 0.10641 | -6.574%
Winter | April | Winter | 34400 | 111 | 41.96% | 3842.92 | 0.11171 | 117372.8 | 10% | 3440 | 11.1 | 544.6667 | 1.7575 | 34400 | 111 | 117372.8 | 1565.2 | 2277.72 | 3842.92 | 0 | 0.11171 | 0% | 1547.434 | 2035.74 | 3583.174 | -259.746 | 0.10416 | -6.759%
Winter | May | Winter | 40640 | 120 | 42.13% | 4311.52 | 0.10609 | 138663.68 | 25% | 10160 | 30 | 1608.6667 | 4.75 | 40640 | 120 | 138663.68 | 1849.12 | 2462.4 | 4311.52 | 0 | 0.10609 | 0% | 1829.1729 | 2200.8 | 4029.9729 | -281.5471 | 0.099163 | -6.53%
Summer | June | Summer | 42560 | 137 | 41.37% | 5371.07 | 0.1262 | 145214.72 | 30% | 12768 | 41.1 | 2021.6 | 6.5075 | 42560 | 137 | 145214.72 | 1936.48 | 3434.59 | 5371.07 | 0 | 0.1262 | 0% | 1910.8671 | 3216.76 | 5127.6271 | -243.4429 | 0.12048 | -4.532%
Summer | July | Summer | 40800 | 132 | 39.18% | 5165.64 | 0.12661 | 139209.6 | 35% | 14280 | 46.2 | 2261 | 7.315 | 40800 | 132 | 139209.6 | 1856.4 | 3309.24 | 5165.64 | 0 | 0.12661 | 0% | 1818.9021 | 3099.36 | 4918.2621 | -247.3779 | 0.12055 | -4.789%
Summer | August | Summer | 44320 | 120 | 39.42% | 5024.96 | 0.11338 | 151219.84 | 35% | 15512 | 42 | 2456.0667 | 6.65 | 44320 | 120 | 151219.84 | 2016.56 | 3008.4 | 5024.96 | 0 | 0.11338 | 0% | 1977.3736 | 2817.6 | 4794.9736 | -229.9864 | 0.10819 | -4.577%
Summer | September | Summer | 34400 | 120 | 40.7% | 4573.6 | 0.13295 | 117372.8 | 10% | 3440 | 12 | 544.6667 | 1.9 | 34400 | 120 | 117372.8 | 1565.2 | 3008.4 | 4573.6 | 0 | 0.13295 | 0% | 1541.183 | 2817.6 | 4358.783 | -214.817 | 0.12671 | -4.697%
Winter | October | Winter | 28640 | 106 | 41.69% | 3478.24 | 0.12145 | 97719.68 | 0% | 0 | 0 | 0 | 0 | 28640 | 106 | 97719.68 | 1303.12 | 2175.12 | 3478.24 | 0 | 0.12145 | 0% | 1287.2299 | 1944.04 | 3231.2699 | -246.9701 | 0.11282 | -7.1%
Winter | November | Winter | 35360 | 107 | 44.2% | 3804.52 | 0.10759 | 120648.32 | 0% | 0 | 0 | 0 | 0 | 35360 | 107 | 120648.32 | 1608.88 | 2195.64 | 3804.52 | 0 | 0.10759 | 0% | 1602.1308 | 1962.38 | 3564.5108 | -240.0092 | 0.10081 | -6.309%
Winter | December | Winter | 33760 | 98 | 44.99% | 3547.04 | 0.10507 | 115189.12 | 0% | 0 | 0 | 0 | 0 | 33760 | 98 | 115189.12 | 1536.08 | 2010.96 | 3547.04 | 0 | 0.10507 | 0% | 1533.5161 | 1797.32 | 3330.8361 | -216.2039 | 0.098662 | -6.095%
| Total Annual |  | 431200 | 114.1667 | 42.43% | 50047.95 | 0.11607 | 1471254.4 | 14.06% | 60608 | --- | 9596.2667 | 2.451 | 431200 | 114.1667 | 1471254.4 | 19619.6 | 30428.35 | 50047.95 | 0 | 0.11595 | 0% | 19416.0632 | 27742.06 | 47158.1232 | -2889.8268 | 0.10915 | -5.905%
| Intensity (per sq.ft./yr) |  | 15.4 | --- | --- | 1.7874 | --- | 52.5448 | --- | 2.1646 | --- | 0.34272 | 8.7536e-05 | 15.4 | 0.0040774 | 52.5448 | 0.7007 | 1.0867 | 1.7874 | 0 | 4.141e-06 | --- | 0.69343 | 0.99079 | 1.6842 | -0.10321 | 3.8981e-06 | ---
[6 empty] | Total Baseline Site EUI: | 79.1662 | kBtu/sq.ft./yr | [6 empty] | Total New Site EUI: | 60.744 | kBtu/sq.ft./yr
Note on C11: Typical heating efficiencies range from 70% for older gas fired equipment to 95% for new high efficiency condensing equipment.
Note on J11: Populate rates by selecting the relevant "Rate Type" and "Utility Rate Structure". For other rates, select "Custom" and enter new rate on the Lookups tab.
Note on C15: Cooling savings would not typically be considered for new construction or end of life replacement where the new heat pump equipment is being compared to new high efficiency cooling equipment.
Note on E19: If New Construction is selected, the "effective implementation cost" considers the difference in cost between the standard efficiency natural gas replacement (including natural gas hook-up and piping) and the high efficiency heat pump replacement. If EOL is selected, the "effective implementation cost" considers the difference in cost between the standard efficiency natural gas replacement and the high efficiency heat pump replacement. If Retrofit is selected, the full cost of the heat pump implementation is considered.
Note on D22: Residential: From contractor input for retrofits, typical total installed cost for a single zone central (ie. hooked up to the existing duct system) large (48kbtu) high efficiency cold climate air source heat pump is around $14,000 - $16,000 for a retrofit. Single zone non-ducted high wall cassette and baseboard systems will be less expensive, whereas single zone non-ducted ceiling cassettes or mini-ducted units will be more expensive. If the loads are smaller, the cost is less. From contractor input for new constuction, total installed costs are typically $12,000 - $15,000. From web research, air source heat pump installed costs are $3,635 - $5,300 for each indoor air handler you install in each room (or zone). The total installed cost for a ducted central air source heat pump system can range from $10,500 - $18,975. Commercial: From contractor input, typical installed cost for a heat pump 10 ton Roof Top Unit is $2,400 - $2,600 per ton. This includes labor, permitting, rigging, and tstat. It does not include electrical installation/modifications.
Note on E22: Residential: From contractor input for retrofits, multi-stage variable speed high efficiency gas furnaces typically cost around $6,500 - $7,500. For multi-stage 18+ SEER AC units, typical costs are around $7,500 - $8,500. The total cost for high efficiency furnace and AC is $14,000 - $16,000. From contractor input for new constuction, total installed costs are typically $12,000 - $15,000. Commercial: From contractor input, typical installed cost for a standard natural gas/ DX RTU is $2,400 - $2,600 / ton. This includes labor, permitting, rigging, tstat. It does not include electrical or gas installation/modifications.
Note on J22: These inputs can be used to test the % rate reductions needed to achieve cost savings.
Note on D24: Typical heat pump water heater costs are between $3,800 and $4,500 depending on whether a new electrical circuit is needed, how far electrical needs to be run, and whether the new heat pump is connecting to intake and/or exhaust ducts.
Note on E24: RS Means 50 gallon water heater cost is $2,400
Note on D25: Residential: For a retrofit, a new electrical circuit for the central heat pump is typically around $1,200. For some existing homes with AC units, you can re-use the existing circuit for the new central heat pump so a new circuit is not needed. For other homes, a new circuit is needed because the existing circuit is not big enough, AC was not in place previously, the existing circuit doesn't meet code, or the heat pump requires an additional circuit for backup heat (not keeping natural gas backup). There will also be electrical cost to add a circuit for the heat pump water heater if it is replacing a natural gas water heater. New construction is expected to have a smaller electrical add, primarily for the heat pump water heater connection. The electrical cost for a new central heat pump should be similar to a new standard AC system. Commercial: Since both RTU scenarios will require electrical for cooling, the full cost of electrical is not included in the new construction option. Retrofits are also assumed to have sufficient electrical supply to the RTUs. Some modification to the eletrical supply may be needed for either scenario, primarily for the heat pump water heater electrical connection, estimated to cost around $1,500 - $2,500.
Note on E26: Residential: Typical cost for natural gas hookup and piping are around $5,000 - $8,000. Commercial: In addition to natural gas hookup, it is estimated that there is a cost of $1,500 - $3,000 to run natural gas piping to each RTU.
Note on J27: Populate rates by selecting the relevant "Rate Type" and "Utility Rate Structure". For other rates, select "Custom" and enter new rate on the Lookups tab.
Note on D28: Residential Based on Xcel Energy rebates: - $400 for 50 gal HP water heater - $300 for standard efficiency heat pump (under 15 SEER, 12.5 EER) or $500 for high efficiency heat pump (15+SEER, 12.5+ EER) Commercial Xcel Energy does not currently have rebates specifically for heat pumps.
Note on D67: Enter data from current utility bills.
Note on L67: See Demand Data tab for additional detail. Defaults should generally be used here unless 15 minute interval data is available for the current heating fuel.
Note on N67: Electric heating will shift the electric peak demand in winter months from mid day to early morning. This column applies a factor to only include the portion of electric heating kW that will add to the baseline peak. The existing peak profile can be reviewed to adjust this estimate, if available. The defaults entered are based on an analysis of past projects (see Demand Data tab).
Note on D92: Enter data from utility bills
Note on F92: The default "On Peak" % values are based on interval meter data from example office projects. These values can be modified if there is bill data or interval data available indicating different percentages.
Note on J92: According to the Commercial Building Energy Consumption Survery (CBECS), cooling energy usually accounts for around 14% of the total building annual electricity use for office buildings. According to the EIA, cooling in homes accounts for around 10% of total annual electricity use on average. https://www.eia.gov/todayinenergy/detail.php?id=10271 The total cooling % may vary depending on other loads and operation of the building.

## Lookups
Typical Values for Inputs
Equipment Efficiencies
|  |  | Electric Resistance/ Electric Boiler | Single Zone RTU Packaged Unit with Heat Pump | Residential Low Ambient Heat Pump
|  | COP @ 47 deg F OAT: | 100% | 360% | 324%
|  | COP @ 17 deg F OAT: | 100% | 230% | 251%
|  | Cooling SEER: | N/A | 12 | 15.8
Heating Efficiencies Lookup
| Month | Avg Low Temp | Electric Resistance/ Electric Boiler | Single Zone RTU Packaged Unit with Heat Pump | Residential Low Ambient Heat Pump
| January | 17 | 100% | 230% | 251%
| February | 20 | 100% | 243% | 258.3%
| March | 26 | 100% | 269% | 272.9%
| April | 34 | 100% | 303.7% | 292.4%
| May | 44 | 100% | 347% | 316.7%
| June | 53 | 100% | 386% | 338.6%
| July | 59 | 100% | 412% | 353.2%
| August | 57 | 100% | 403.3% | 348.3%
| September | 47 | 100% | 360% | 324%
| October | 36 | 100% | 312.3% | 297.2%
| November | 25 | 100% | 264.7% | 270.5%
| December | 17 | 100% | 230% | 251%
Equipment Type Selection Options
| Commercial | Residential | Custom
| Xcel Energy Secondary General (no Time of Use) | Xcel Energy General Residential Plan | Custom
| Xcel Energy Primary General (Time of Use) | Xcel Energy Time of Use Pricing Residential
Xcel Energy Peak Demand Pricing Residential
Commercial Utility Rates
Xcel Energy Secondary General (no Time of Use)
| $/Peak kW | $/kWh on Peak | $/kWh off Peak
Summer | 25.07 | 0.0455 | 0.0455
Winter | 20.52 | 0.0455 | 0.0455
Summer Months: | Jun to Sep
On Peak Times: | NA
Xcel Energy Primary General (Time of Use)
| $/Peak kW | $/kWh on Peak | $/kWh off Peak
Summer | 23.48 | 0.0534 | 0.0389
Winter | 18.34 | 0.0534 | 0.0389
Summer Months: | Jun to Sep
On Peak Times: | 9a-9p
Residential Utility Rates
Xcel Energy General Residential Plan | [9 empty] | Xcel Energy Residential Rates - 4/21/2020
| $/Peak kW | $/kWh on Peak | $/kWh off Peak |  | First 500 kWh | Above 500 kWh | % > 500 kWh
Summer | 0 | 0.106 | 0.106 |  | 0.1 | 0.14 | 15%
Winter | 0 | 0.09 | 0.09 |  | 0.09 | 0.09 | --
Summer Months: | Jun to Sep
On Peak Times: | 9a-9p
Xcel Energy Time of Use Pricing Residential
| $/Peak kW | $/kWh Day Time Average | $/kWh off Peak |  | $/kWh Shoulder | $/kWh on Peak | % On Peak
Summer | 0 | 0.155 | 0.08 |  | 0.13 | 0.18 | 50%
Winter | 0 | 0.098 | 0.07 |  | 0.09 | 0.13 | 20%
Summer Months: | Jun to Sep
On Peak Times: | 9a-9p
Xcel Energy Peak Demand Pricing Residential
| $/Peak kW | $/kWh on Peak | $/kWh off Peak
Summer | 15.34 | 0.04 | 0.03
Winter | 12.58 | 0.04 | 0.02
Summer Months: | Jun to Sep
On Peak Times: | 9a-9p
Custom | Enter values for custom rate
Custom
| $/Peak kW | $/kWh on Peak | $/kWh off Peak
Summer | 25 | 0.05 | 0.05
Winter | 25 | 0.05 | 0.05
Summer Months: | Jun to Sep
On Peak Times: | 9a-9p
First Cost Information
See calculator tab for notes on cost ranges
Residential - End of Life |  |  | Heat Pump |  | Natural Gas |  |  | Heat Pump | Natural Gas
*Both options assume high efficiency equipment |  |  | Low | High | Low | High |  | Price used
Central heating/cooling system (including install) |  |  | 14000 | 16000 | 14000 | 16000 |  | 15000 | 15000
Tank type domestic hot water heater |  |  | 3800 | 4500 | 2000 | 3000 |  | 3300 | 2600
Electrical modification |  |  | 0 | 1200 |  |  |  | 2100
Natural gas connection and piping (NC only) | [8 empty] | 6500 | Cost Delta
Totals |  |  | 17800 | 21700 | 16000 | 19000 |  | 20400 | 17600 | 15.91%
Cost Delta |  |  |  |  | 1800 | 2700 |  |  | 2800
Residential - New Construction |  |  | Heat Pump |  | Natural Gas |  |  | Heat Pump | Natural Gas
*Both options assume high efficiency equipment |  |  | Low | High | Low | High |  | Price used
Central heating/cooling system (including install) |  |  | 12000 | 15000 | 12000 | 15000 |  | 13000 | 13000
Tank type domestic hot water heater |  |  | 3800 | 4500 | 2000 | 3000 |  | 3100 | 2400
Electrical modification |  |  | 0 | 1200 |  |  |  | 500
Natural gas connection and piping (NC only) |  |  |  |  | 5000 | 8000 |  |  | 6500 | Cost Delta
Totals |  |  | 15800 | 20700 | 19000 | 26000 |  | 16600 | 21900 | -24.2%
Cost Delta |  |  |  |  | -3200 | -5300 |  |  | -5300
|  | # of Units | 9
|  | Tons per Unit | 10
|  | Total Tons | 90
Commercial - End of Life |  |  | Heat Pump |  | Natural Gas |  |  | Heat Pump | Natural Gas
*Both options assume high efficiency equipment |  |  | Low | High | Low | High |  | Price used
Central heating/cooling system (including install) |  |  | 216000 | 234000 | 216000 | 234000 |  | 234000 | 234000
Average cost per ton |  |  | 2400 | 2600 | 2400 | 2600 |  | 2600 | 2600
Tank type domestic hot water heater |  |  | 3800 | 4500 | 2000 | 3000 |  | 4200 | 2600
Electrical modification |  |  | 2000 | 2000 |  |  |  | 3000
Natural gas connection and piping (NC only) | [9 empty] | Cost Delta
Totals |  |  | 221800 | 240500 | 218000 | 237000 |  | 241200 | 236600 | 1.944%
[5 empty] | 3800 | 3500 |  |  | 4600
Commercial - New Construction |  |  | Heat Pump |  | Natural Gas |  |  | Heat Pump | Natural Gas
*Both options assume high efficiency equipment |  |  | Low | High | Low | High |  | Price used
Central heating/cooling system (including install) |  |  | 216000 | 234000 | 216000 | 234000 |  | 216000 | 216000
Average cost per ton |  |  | 2400 | 2600 | 2400 | 2600 |  | 2400 | 2400
Tank type domestic hot water heater |  |  | 3800 | 4500 | 2000 | 3000 |  | 3800 | 2400
Electrical modification |  |  | 2000 | 2000 |  |  |  | 1500
Natural gas connection and piping (NC only) |  |  |  |  | 16000 | 27000 |  |  | 21000 | Cost Delta
Totals |  |  | 221800 | 240500 | 234000 | 264000 |  | 221300 | 239400 | -7.561%
[5 empty] | -12200 | -23500 |  |  | -18100
Note: This sheet provides references of typical values that can be used as inputs on the calculator tab.
Note on E7: Efficiencies are based on Trane Precedent WHC High Efficiency Heat Pump
Note on F7: Efficiencies are based on the Mitsubishi M-Series equipment: SVZ-KP36NA & SUZ-KA36NA2
Note on E11: Trane air source Precedent high efficiency heat pump RTU has the following SEERs: - 3-5 tons have SEER of 16-16.5 - 6-10 tons have SEER of 11.5-12.1
Note on C14: Values from: https://www.usclimatedata.com/climate/denver/colorado/united-states/usco0105
Note on H53: Celeste Cizik: % determined from example residential data for a 3,000 sq.ft. house.
Note on B67: Peak charges are sum of distribution demand charge and generation and transmission demand change

## Net Present Costs
Energy Project Economic Analysis |  | =input |  |  | Escalation Factors/Discount Rate
Base Year: | 2020 |  |  |  | Electric Energy Cost |  |  | 2%
[5 empty] | Gas Energy Cost |  |  | 1%
[5 empty] | All Other Costs |  |  | 1.3%
[5 empty] | Discount Rate |  |  | 8%
Natural Gas
| Project Years | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15
|  | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | TOTAL
Investment Costs
| First Cost | 236600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 236600
| Design/Support | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Recurring Expenses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Investment Sub Total | 236600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 236600
| Present Value of Inv | 236600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 236600
Operating Variance: (Costs)/Savings
| Electric Energy Cost |  | 50047.95 | 51048.909 | 52069.8872 | 53111.2849 | 54173.5106 | 55256.9808 | 56362.1205 | 57489.3629 | 58639.1501 | 59811.9331 | 61008.1718 | 62228.3352 | 63472.9019 | 64742.36 | 66037.2072 | 865500.0652
| Gas Energy Cost |  | 4983.08 | 5032.9108 | 5083.2399 | 5134.0723 | 5185.413 | 5237.2672 | 5289.6398 | 5342.5362 | 5395.9616 | 5449.9212 | 5504.4204 | 5559.4646 | 5615.0593 | 5671.2099 | 5727.922 | 80212.1182
| Maintenance Cost |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating Exp Sub Total |  | 55031.03 | 56081.8198 | 57153.1271 | 58245.3572 | 59358.9237 | 60494.248 | 61651.7603 | 62831.8991 | 64035.1117 | 65261.8543 | 66512.5922 | 67787.7998 | 69087.9612 | 70413.5698 | 71765.1291 | 945712.1834
| Present Value of Op Costs |  | 50954.6574 | 48081.1212 | 45369.995 | 42812.0764 | 40398.686 | 38121.6377 | 35973.21 | 33946.12 | 32033.4985 | 30228.8659 | 28526.1107 | 26919.468 | 25403.5 | 23973.0773 | 22623.3617 | 525365.3857
Residual Value
| Residual Total Value | 236600 | 55031.03 | 56081.8198 | 57153.1271 | 58245.3572 | 59358.9237 | 60494.248 | 61651.7603 | 62831.8991 | 64035.1117 | 65261.8543 | 66512.5922 | 67787.7998 | 69087.9612 | 70413.5698 | 71765.1291 | 1182312.1834
| Residual Present Value | 236600 | 50954.6574 | 48081.1212 | 45369.995 | 42812.0764 | 40398.686 | 38121.6377 | 35973.21 | 33946.12 | 32033.4985 | 30228.8659 | 28526.1107 | 26919.468 | 25403.5 | 23973.0773 | 22623.3617 | 761965.3857
| Net Present Cost | 0 2020: 761965.3857
Heat Pump (with Rebate and Current Rates)
| Project Years | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15
|  | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | TOTAL
Investment Costs
| First Cost | 241200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 241200
| Design/Support | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Recurring Expenses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Investment Sub Total | 241200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 241200
| Present Value of Inv | 241200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 241200
Operating Variance: (Costs)/Savings
| Electric Energy Cost |  | 55617.1945 | 56729.5384 | 57864.1292 | 59021.4117 | 60201.84 | 61405.8768 | 62633.9943 | 63886.6742 | 65164.4077 | 66467.6958 | 67797.0498 | 69152.9908 | 70536.0506 | 71946.7716 | 73385.707 | 961811.3323
| Gas Energy Cost |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Maintenance Cost |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating Exp Sub Total |  | 55617.1945 | 56729.5384 | 57864.1292 | 59021.4117 | 60201.84 | 61405.8768 | 62633.9943 | 63886.6742 | 65164.4077 | 66467.6958 | 67797.0498 | 69152.9908 | 70536.0506 | 71946.7716 | 73385.707 | 961811.3323
| Present Value of Op Costs |  | 51497.4023 | 48636.4355 | 45934.4113 | 43382.4996 | 40972.3607 | 38696.1185 | 36546.3341 | 34515.9822 | 32598.4276 | 30787.4039 | 29076.9926 | 27461.6041 | 25935.9594 | 24495.0728 | 23134.2354 | 533671.24
Residual Value
| Residual Total Value | 241200 | 55617.1945 | 56729.5384 | 57864.1292 | 59021.4117 | 60201.84 | 61405.8768 | 62633.9943 | 63886.6742 | 65164.4077 | 66467.6958 | 67797.0498 | 69152.9908 | 70536.0506 | 71946.7716 | 73385.707 | 1203011.3323
| Residual Present Value | 241200 | 51497.4023 | 48636.4355 | 45934.4113 | 43382.4996 | 40972.3607 | 38696.1185 | 36546.3341 | 34515.9822 | 32598.4276 | 30787.4039 | 29076.9926 | 27461.6041 | 25935.9594 | 24495.0728 | 23134.2354 | 774871.24
| Net Present Cost | 0 2020: 774871.24
Heat Pump (with Rebate and Reduced Rates)
| Project Years | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15
|  | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | TOTAL
Investment Costs
| First Cost | 241200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 241200
| Design/Support | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Recurring Expenses | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Investment Sub Total | 241200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 241200
| Present Value of Inv | 241200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 241200
Operating Variance: (Costs)/Savings
| Electric Energy Cost |  | 52395.2555 | 53443.1606 | 54512.0238 | 55602.2643 | 56714.3096 | 57848.5958 | 59005.5677 | 60185.679 | 61389.3926 | 62617.1805 | 63869.5241 | 65146.9146 | 66449.8529 | 67778.8499 | 69134.4269 | 906092.9977
| Gas Energy Cost |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Maintenance Cost |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operating Exp Sub Total |  | 52395.2555 | 53443.1606 | 54512.0238 | 55602.2643 | 56714.3096 | 57848.5958 | 59005.5677 | 60185.679 | 61389.3926 | 62617.1805 | 63869.5241 | 65146.9146 | 66449.8529 | 67778.8499 | 69134.4269 | 906092.9977
| Present Value of Op Costs |  | 48514.1255 | 45818.8963 | 43273.402 | 40869.3241 | 38598.8061 | 36454.428 | 34429.182 | 32516.4497 | 30709.9803 | 29003.8702 | 27392.5441 | 25870.7361 | 24433.473 | 23076.0578 | 21794.0546 | 502755.3299
Residual Value
| Residual Total Value | 241200 | 52395.2555 | 53443.1606 | 54512.0238 | 55602.2643 | 56714.3096 | 57848.5958 | 59005.5677 | 60185.679 | 61389.3926 | 62617.1805 | 63869.5241 | 65146.9146 | 66449.8529 | 67778.8499 | 69134.4269 | 1147292.9977
| Residual Present Value | 241200 | 48514.1255 | 45818.8963 | 43273.402 | 40869.3241 | 38598.8061 | 36454.428 | 34429.182 | 32516.4497 | 30709.9803 | 29003.8702 | 27392.5441 | 25870.7361 | 24433.473 | 23076.0578 | 21794.0546 | 743955.3299
| Net Present Cost | 0 2020: 743955.3299

## Demand Data
Average Load Factor from Example Projects
Load Factor = energy consumed/(peak power*days/month*24)
Average Building Load Factor Used
| Month | LF %
| Jan | 44.79% |  |  |  |  | AVG WINTER LF | 42.49%
| Feb | 45.24% |  |  |  |  | AVG SUMMER LF | 20.87%
| Mar | 28.08% |  |  |  |  | AVG SHOULDER LF | 22.86%
| Apr | 26.24%
| May | 18.33%
| Jun | 19.15%
| Jul | 24.23%
| Aug | 19.22%
| Sep | 13.63%
| Oct | 28%
| Nov | 34.61%
| Dec | 45.32%
Building 1 Monthly Data
| Month | Days/ Month | Energy Use (kWh/SF/ month) | B1 Peak Demand (kW/SF) | LF %
| Jan | 31 | 0.88973 | 0.0024967 | 47.9% |  | AVG WINTER LF | 42.41%
| Feb | 28 | 0.75269 | 0.0025267 | 44.33% |  | AVG SUMMER LF | 20.17%
| Mar | 31 | 0.58162 | 0.00248 | 31.52% |  | AVG SHOULDER LF | 23.1%
| Apr | 30 | 0.38307 | 0.00197 | 27.01%
| May | 31 | 0.28241 | 0.00239 | 15.88%
| Jun | 30 | 0.11396 | 0.00080667 | 19.62%
| Jul | 31 | 0.096863 | 0.00068 | 19.15%
| Aug | 31 | 0.081373 | 0.00050333 | 21.73%
| Sep | 30 | 0.11848 | 0.00121 | 13.6%
| Oct | 31 | 0.47905 | 0.0023433 | 27.48%
| Nov | 30 | 0.66036 | 0.0029233 | 31.37%
| Dec | 31 | 0.88447 | 0.0025833 | 46.02%
Building 2 Monthly Data
| Month | Days/ Month | Energy Use (kWh/SF/ month) | B1 Peak Demand (kW/SF) | LF %
| Jan | 31 | 1.3065 | 0.0042133 | 41.68% |  | AVG WINTER LF | 42.57%
| Feb | 28 | 1.3065 | 0.0042133 | 46.14% |  | AVG SUMMER LF | 21.57%
| Mar | 31 | 0.5819 | 0.0031733 | 24.65% |  | AVG SHOULDER LF | 22.62%
| Apr | 30 | 0.5819 | 0.0031733 | 25.47%
| May | 31 | 0.42106 | 0.0027233 | 20.78%
| Jun | 30 | 0.065477 | 0.00048667 | 18.69%
| Jul | 31 | 0.063963 | 0.00029333 | 29.31%
| Aug | 31 | 0.065473 | 0.00052667 | 16.71%
| Sep | 30 | 0.15026 | 0.0015267 | 13.67%
| Oct | 31 | 0.76339 | 0.0035967 | 28.53%
| Nov | 30 | 1.0218 | 0.00375 | 37.84%
| Dec | 31 | 1.3886 | 0.0041833 | 44.62%
Building 3 Monthly Data
This is an electric building that had 24/7 operation. Not representative of a typical office schedule but could be used for a 24/7 building.
| Month | Days/ Month | On Peak kWh | Off Peak kWh | Total kWh | Peak kW | LF % | % On Peak
| Jan | 30 | 77936.9439 | 176041.0561 | 253978 | 408 | 86.46% | 44.27% | AVG WINTER LF | 80.94%
| Feb | 30 | 77936.9439 | 176041.0561 | 253978 | 408 | 86.46% | 44.27% | AVG SUMMER LF | 59.66%
| Mar | 30 | 77936.9439 | 134417.0561 | 212354 | 376 | 78.44% | 57.98% | AVG SHOULDER LF | 61.24%
| Apr | 29 | 68881 | 95366 | 164247 | 501 | 47.1% | 72.23%
| May | 29 | 80873 | 81109 | 161982 | 448 | 51.95% | 99.71% | AVG WINTER On Peak kWh | 47.12%
| Jun | 32 | 96564 | 101526 | 198090 | 473 | 54.53% | 95.11% | AVG SUMMER On Peak kWh | 76.76%
| Jul | 30 | 88375.26 | 130753.74 | 219129 | 499.3451 | 60.95% | 67.59% | AVG SHOULDER On Peak kWh | 69.54%
| Aug | 29 | 96599 | 142921 | 239520 | 542 | 63.49% | 67.59%
| Sep | 32 | 88620 | 142720 | 231340 | 470 | 64.09% | 62.09%
| Oct | 29 | 75948 | 136406 | 212354 | 472 | 64.64% | 55.68%
| Nov | 33 | 82294 | 171684 | 253978 | 428 | 74.93% | 47.93%
| Dec | 31 | 87735 | 168765 | 256500 | 454 | 75.94% | 51.99%
Winter Peak Load Profiles
Building without electric heat
Building with electric heat
[11 empty] | Demand from heating = | 2020-01-08 | 2020-01-12 | 2020-02-10 | 2020-03-08
[11 empty] | Base night load | 139 | 178 | 155 | 88
[11 empty] | Heating peak | 334 | 430 | 367 | 319
[11 empty] | Day time peak | 247 | 233 | 248 | 250
[11 empty] | Portion of peak from heating | 195 | 252 | 212 | 231
[11 empty] | Increase in peak | 87 | 197 | 119 | 69
[11 empty] | % of total heat peak | 44.62% | 78.17% | 56.13% | 29.87%
Note: This sheet is used to calculate an average monthly load factor which is a relationship between monthly energy use and peak demand. The average load factor is used in the electrification calculator to determine the estimated peak electrical demand each month given the input of the monthly energy use. The monthly values in this sheet were determined by analyzing data from past projects that had heating interval data available.